## Slide 1: Preliminary design of a High Pressure Steam Turbine
Rossi Andrea
Politecnico di Milano

## Slide 2: The design specifications
The project consist in the preliminary design of the high pressure part of a steam turbine. The design process requires some initial data other than many other assumptions.
Inlet flow characteristics, in terms of total quantities, are:
pT = 150 bar
TT = 700◦C
The stages must provide a pressure ratio β of 2.5.
Since the first stage of the design is the first stage of the whole machine, the inlet direction is assumed to be purely axial.
10 of 62

## Slide 3: The model of the fluid
The text leave the choice of the model of the fluid to our responsibility. The two main alternatives are:
perfect gas with γ = 1.33 and constant cp
steam tables
Since steam tables are available as an additional library in Matlab, to guarantee a better precision they are used. In particular the library XSteam is applied in any calculation of steam properties.
10 of 62

## Slide 4: The design process
Most of the choices related to the machine are taken based not only on common techniques like loading criteria, but also on the comparison of the result from the implementation of the model in computer code.
The machine will be implemented in a power plant, so the first goal of the design is
highest efficiency as possible
10 of 62

## Slide 5: The model of the machine - The inputs
The data available from the costumer are necessary but not sufficient. So as additional and more specific input we take:
the reaction degree in the middle diameter χ,
the rotational speed n in rpm,
the number of stages,
the flow coefficient φ = va/U,
the minimum value of blade height over the diameter b/Dmid,
the partial admission coefficient ε,
the blade solidity σ = chord/pitch
the ratio of the chord over the blade height
10 of 62

## Slide 6: The model of the machine - The inputs
the blade thickness over the chord
the absolute clearance
the number of seals per rotor
an initial guess of the efficiency (η = 1 could be a guess)
the number of section in which divide the span
other numerical and computational parameters
  the maximum number of iterations
  the tolerances (1 · 10−6)
10 of 62

## Slide 7: The model of the machine - The inputs
Some of the input are trivial and mandatory, but other are chosen. For example the number of stages is taken as input but it could also be the result of the calculation.
In fact the alternative was to choose the work coefficient λ = l/U2, and in that case the number of stages would have been the result.
Since the number of stages is a very significant parameter respect to the work coefficient this choice has been made.
Another parameter is the flow coefficient that can be replaced with
kp = U/v1
10 of 62

## Slide 8: The model of the machine - The main loop
The whole process requires the total efficiency of the machine. The efficiency is also an output of the design: ⇒ iterative loop.
Initial guess of ηT T
Perform the design of the machine
OLD
T T T T
|η − η | < toll
Loop again
Convergence reached
yes
no
10 of 62

## Slide 9: The model of the machine - The main loop
h0 = h(p0 , T0 ) (1)
T T T
To compute the isoentropic outlet enthalpy we have simply to consider that the initial final entropy are the same by definition.
s0 = s0 = s(p0 , T0 ) (2)
T T T
end
hT
isoentropic
p
0
βT T
( \
= h T , s0 (3)
Finally we calculate the outlet enthalpy from the efficiency:
T
T
T T
T
end 0 0 end
Tis
h = h − η · (h − h )
(4)
10 of 62

## Slide 10: The model of the machine - The main loop
Dividing the enthalpy drop by the stages number we find the enthalpy drop of the single stage that is also the Euler work of the stage.
le = u · (v1T − v2T ) =
h − h
0 end
T T
Nstages
(5)
The main first quantity in which we are interested is the peripheral speed U. We can obtain it from the mass flow rate:
1
0 A 0 A
m˙ = ρ · v · S = ρ · v · π
b
Dmid
( \
D
2
mid
(6)
Having defined both φ = vA/U and Dmid = 60/(2 π n) U the mass flow rate is only function of the the cube of the peripheral speed.
1The static density is unknown but since we are iterating we keep the total one
as first guess ad we update it at every cycle
10 of 62

## Slide 11: The model of the machine - The velocity triangle
To design the velocity triangle we have to make some hypothesis:
repeated stage, so v0 = v2
constant axial velocity v1A = v2A = v3A = vA
the first stator has an axial inlet so it can break the repeated stage rule. In this case its velocity will be v0 = vA
Now what we need are:
U previously found from equation 6;
vA = φ · U
l
∆vT = − U = v1T − v2T
v1T + v2T = 2 U · (1 − χmid)
10 of 62

## Slide 12: The model of the machine - The velocity triangle
As we can see in figure 1 the outlet velocity of the stage is almost but not exactly axial.
The first stage will have a reaction degree at midspan slightly different from the desired.
↑ u
v1 → v2 → ← w1
← w2
↑ u
Figure: Example of result of a velocity triangle
10 of 62

## Slide 13: The model of the machine - The inlet of the machine
0
T
0
h = h +
1
0
T
⇒ h = h −
After the definition of the velocity triangle the next step is the thermodynamical analysis, and we start from point 0. From the definition of total entropy we can get the static one:
v2 v2
0 A
2 2
(7)
To get the static pressure and temperature we have to remember that:
•
0
T
0 0 0
T T
the static entropy is equal to the total entropy s = s = s(p , T ).
But we can obtain the static pressure remembering that the total pressure is obtained stopping the flow in an isoentropic way and measuring the pressure.
p0 = p(s0, h0)
(8)
From the two thermodynamical quantities we can obtain all the others.
10 of 62

## Slide 14: The model of the machine - Losses definition
In point 0 we know everything so we can calculate the blade height:
0
b =
m˙
ρ0 π Dmid vA ε
(9)
To perform the thermodynamical analysis of the stator we have to introduce the calculation of the losses. In particular according to the definition of the total pressure loss.
Y
stator
pT 0 − pT 1
=
pT 1 − p1
(10)
Yrotor =
p − p
rel rel
T 1 T 2
rel
T 1
p − p
2
(11)
T
Where prel is the total pressure in the relative frame.
10 of 62

## Slide 15: The model of the machine - Solution of the stator
If we obtain the loss coefficient we are able to find all the thermodynamical quantities at the outlet of the stator (Point 1). The solution is a bit trickier than the previous since it is iterative. Both pT 1 and p1 shares the same entropy that is unknown. In both cases we know enthalpy but as known we miss another quantity.
Substituting pT 1 and p1 into equation 10 leave that equation with just the entropy as unknown.
stator
pT 1(hT 1, s) − p1(h1, s)
pT 0 − pT 1(hT 1, s)
Y − = 0 (12)
where: h = h
1 T 1
2
− v /2 = h
T 0
2
1 1
− v /2.
Equation 12 is implicit and non-linear and have to be solved numerically since requires the computation of the steam table. We apply the secants method to get a solution in terms of entropy.
10 of 62

## Slide 16: The model of the machine - Solution of the rotor
The same procedure can be applied to the rotor with the difference that in this case we use relative quantities.
rel
w2
( \
pT = p h + 2 , s (13)
2
T 2 T 1
h = h − = h −
w2 w2
rel 2 rel 2
2 2
(14)
Total relative enthalpy conserves along the rotor in an axial machine.
Yrotor −
rel rel rel
T 1 T 2 T 2
p − p (h , s)
rel rel
T 2 T 2
2 2
p (h , s) − p (h , s)
= 0 (15)
We solve equation 15 numerically as the stator case, and from the entropy the solve completely the outlet of the rotor.
16 of 62

## Slide 17: The model of the machine - Span evolution
Up to now we have only considered each section uniform along the span. Clearly this is an approximation since the peripheral speed u changes with the radius.
To improve the quality of the result we consider that the velocity triangles evolve along the span with a specific rule.
The approach chosen is the constant angle. It cannot guarantee that the work is constant along the blade height, but since the is only few centimetre height, this approach is good enough.
ADVANTAGE ⇒ Lower manufacturing cost.
We can solve the velocities along the span considering:
the radial equilibrium,
vT /vA = tan(α1) = constant.

## Slide 18: The model of the machine - Span evolution
Applying the previous relation into the radial equilibrium we obtain:
A ∂r r ∂r
v and
∂vA + vT ∂(r vT ) = 0 v
T
vA
= tan(α1) (16)
The solution to equation 16 is:




A
mid
A
v (r) = v ·
r
mid
r
( \ 2
1
sin (α )
T A 1
v (r) = v (r) · tan(α )
T T 1 T 2
l(r) = u ∆v = ω r (v (r) − v (r)) /= constant
For the rotor is the same except that we substitute the absolute velocity with the relative one

## Slide 19: Figure: Sketch of velocity and angle evolution in a stator.
0.225
0.23
0.235
0.255
0.26
0.265
0.24 0.245 0.25
Radius (m)
140
160
180
200
220
240
260
280
300
320
340
Velocity (m/s)
0
10
20
30
40
50
60
70
Angle (degrees)
vA1
vT1
U
alpha0
alpha1

## Slide 20: The model of the machine - Section solution
The span velocity is required to compute a better value for the blade height from the mass flow rate.
r
r
tip
rhub
m˙ = ρ(r) · 2 π r · vA(r)dr (17)
Equation 17 cannot be solved analytically to find b = rtip − rhub since the density depends on the steam table.
The solution in to approximate the integral with a summation for some points along the span. The number of point is taken as an input, but their location is chosen smartly.
The solution is in the form:
N points
N points
, ,
m˙ ~ wi · vAi πDmid ε b = b · πDmid ε · wi · vA(ri)
i i
( \
(18)

## Slide 21: The model of the machine - Section solution
The radius at which we compute the solution are chosen according to the following rule:
i
r =
D − b
mid
2
+ xi · b (19)
Where the first guess of b is taken from the midspan solution. The coefficients xi and wi are taken form the Legendre-Gauss quadrature technique. For the case of 4 points for example the coefficients result:
xi | wi
0.9306 | 0.1739
0.67 | 0.3261
0.33 | 0.3261
0.0694 | 0.1739

## Slide 22: Figure: Influence of the choise of the number of Gauss points
1
2
3
4
7
8
9
10
1
0.99998
0.99996
0.99994
0.99992
0.9999
0.99988
0.99986
0.99984
5 6
Gauss Points
Sum of blade heights of all stages (normalized)
 |  |  |  |  |  |  | Number Number Number Number Number Number Number Number |  | of of of of of of of of | stages stages stages stages stages stages stages stages |  | = = = = = = = = | 1 2 3 4 5 6 7 8 | 
We can notice that the difference is absolutely negligible for a number of Gauss points greater than 2. For safety region we will use 4 points to be sure not to lose precision and to have a better span evolution

## Slide 23: The model of the machine - Section solution
So we start a new iterative process to find the correct value of the blade height.
In this process we need the pressure along the span.
⇒ We have to pass from the loss coefficient.
Loss coefficient accounts for 3 contributions:
profile losses ← local property
clearance losses ← global property
secondary losses ← global property
So along the span we compute the specific profile losses that depends on the velocity triangle, but we keep the others from the midspan.
Doing this we have made the strong assumption that the fluid flows along almost parallel streamlines.

## Slide 24: So we have two other iterative loops inside the main one.
Initial guess of b from initial point
Solve stator midspan
Solve stator along the span and calculate a new value for b
Loop again
b of the stator
Solve rotor midspan
Solve rotor along the span and calculate a new value for b
|bold − b| < toll
Loop again
b of the rotor
STAGE SOLVED! Start with the next one.
yes
no
|bold − b| < toll
yes
no

## Slide 25: The model of the machine - The end of the loop
Repeating the loop sketched in the previous slide for all the stages we completely solve the thermodynamics of all the points of interest.
From all the data we collect we can verify that the total pressure ratio is that desired and we can compute the efficiency of each stage.
Finally we can calculate the most important parameter, the total to total efficiency that we have guess at the beginning.
Tend
T
hisoentropic = h(pend, s0)
(20)
ηTT =
T 0
h − h
end
T
T 0
h − h
isoentropic
Tend
(21)
If convergence is not reached the main loop start again.

## Slide 26: The model of the machine - Effective work
Applying constant angle methodology the work is not constant along the span, so per each stage we can compute the effective work and compare to the real one.
If the difference is significant we have to redesign the velocity triangles to guarantee that the expansion work is that desired. We can take a mean along the span weighting on the mass flow or on the Gauss weight.
l ~
),
N points
i
i
w · u · (w − w
i i 1T 2T
i
) · π D
b · ρ v
mid i Ai
m˙
(22)
The difference due to small blade height in high pressure part of the turbine is negligible.

## Slide 27
1.5
2
2.5
3
6
6.5
7
7.5
8
0
1
2 · 10−2
4 · 10−2
6 · 10−2
8 · 10−2
0.1
0.12
0.14
3.5 4 4.5 5 5.5
Number of stages
Error of the mean work (In percentage)
n = 3000
n = 4500
n = 6000
n = 7500
n = 9000
n = 10500
n = 12000

## Slide 28
1.5
2
2.5
3
6
6.5
7
7.5
8
2.4
1
2.5
2.6
2.7
2.8
2.9
3
3.5 4 4.5 5 5.5
Number of stages
Effective compression ratio βT T
 |  |  |  |  |  |  |  |  |  | b/Dm = 0.025 b/Dm = 0.077778 b/Dm = 0.13056 b/Dm = 0.18333 b/Dm = 0.23611 b/Dm = 0.28889 b/Dm = 0.34167 b/Dm = 0.39444 b/Dm = 0.44722 b/Dm = 0.5 |  |  |  | 
In mid or low pressure turbine the assumption could be not true.

## Slide 29: The model of the machine - The losses
Up to now we have simply spoken of rotor and stator losses in a generic way without explaining how to evaluate them. The losses are divided in 3 groups:
Profile losses;
Secondary losses;
Clearance losses.
As previously stated the last two are evaluated by the model as mean losses along the section.
The calculation of profile losses is performed according to the
Ainley-Mathieson correlation.
The calculation of others instead is performed according to the
Dunham-Came correlation.

## Slide 30: The model of the machine - Profile losses
0.2
0.4
0.6
0.8
1
1.2
0.02
0.04
0.06
0.08
s 1
=
c solidity
Profile losses Yp
10
15
20
25
30
40
50
0.2
0.4
0.6
0.8
1
0.05
0.10
0.15
0.20
0.25
s
1
=
c solidity
Profile losses Yp
Profile losses are calculated in a general case with a linear interpolation between:
axial inlet with χ = 0.5 (α0 = 0)
symmetrical blades (α0 = −α1)
Profile losses (axial inlet) Profile losses (symmetric blades)
0.10 0.30
α1 = 10
15
20
25
30
40
50

## Slide 31: The model of the machine - Profile losses
reference
We compute the total pressure losses in both cases and than we apply the following interpolation:
2
α
A B A
Yp = Y + m (Y − Y )
(23)
Where mα = −α0/α1. Then we apply further corrections:
Max thickness: Yp = Ypref ·
(
t /c
max
t
/c|
max ref
\mα
Reynolds: Yp = Ypref ·
(
Re
ref
Re
\
0.2
p
pref
(
Trailing edge: Y = Y · 1 + 7 −
t t
s s
1
1
ref
( \\
Where the Reynolds number is that referred to the chord and values:
ρ0 v c
Re =
µ0
(24)

## Slide 32: The model of the machine - The solidity
The main parameter that influences profile losses is the solidity Even if it can be chosen arbitrarily it must be subjected to the number of blades that is instead an integer. So the solidity is computed passing through a rounding operation.
blades
N = round
π D
mid
c
( \
σ (25)
And then we recalculate the solidity.
c c
σ = =
s π D
mid
Nblades
(26)
Than when we calculate profile losses along the span we keep that number of blades and recalculate the solidity in the same way as equation 26 with the new value of the diameter.

## Slide 33: The model of the machine - Secondary losses
Secondary losses are accounted as follow:
secondary
Y = 0.0334
1
cos(α )
cos(α0)
H
(27)
c
H = 4 (tan α0 − tan α1) b
2
cos2(α1)
m
cos(α )
(28)
tan α
m
2
tan α0 + tan α1
= (29)
Every loss equation in the way it is written holds for a stator, for a rotor instead we must replace
α0 ⇔ β1
α1 ⇔ β2

## Slide 34: The model of the machine - Clearance losses
Secondary losses are accounted as follow:
Yclearance = B
k
c
( \
0.78
H (30)
Where H has been previously defined in equation 28 The term k is the clearance normalized respect to the number of seals.
k =
clearance
seals number
( \
0.42
(31)
The coefficient B distinguish between the stator and the rotor and for the type of casing.



0
B = 0.37
0.47
stator
shrouded rotor
unshrouded rotor

## Slide 35: The choice of parameters - Reference condition
When testing many configurations, we keep for parameters which are note analysed the following values:
solidity σ = 1.225
number of stages nstages = 4
rotational speed n = 6000 rpm
reaction degree at midspan χ = 0.5
flow coefficient φ = 0.5
partial admission ε = 1
blade height over mean diameter b/Dmid = 0.05
blade height over chord b/Dmid = 0.5
seals number = 2
clearance k = 0.0006 m

## Slide 36: The choice of parameters - The solidity
0.85
0.84
0.83
0.82
0.86
0.87
0.88
0.93
0.92
0.91
0.9
0.89
0.94
etaTT
 |  |  |  |  | nStages = 1 nStages = 2 nStages = 3 |  | 
 |  |  |  |  | nStages = 4 nStages = 5 nStages = 6 |  | 
 |  |  |  |  |  | nStages = 7 | 
 |  |  |  |  | nStages = 8 |  | 
0.85
0.86
0.87
0.88
0.89
0.9
0.91
0.92
0.93
0.94
0.95
1 | 1.1 | 1.2 | 1.3 | 1.4 | 0.84 1 | 1.1 | 1.2 | 1.3 | 1.4
 |  | solidity |  |  |  |  | solidity |  | 
etaTT
n = 3000
n = 4500
n = 6000
n = 7500
n = 9000
n = 10500
n = 12000

## Slide 37: The choice of parameters - The solidity
0.92
0.93
etaTT
chiMID = 0.35
chiMID = 0.4
chiMID = 0.45
chiMID = 0.5
chiMID = 0.55
0.96
0.95
0.94
0.93
0.92
0.91
0.9
0.89
0.88
0.87
0.86
0.85
0.84
etaTT
chordsub = 0.25
chordsub = 0.5
chordsub = 0.75
chordsub = 1
chordsub = 1.25
chordsub = 1.5
chordsub = 1.75
chordsub = 2
0.83
1
1
1.1
1.2
solidity
1.3
1.4
1.1
1.2 1.3
solidity
1.4
37 of 62

## Slide 38: The choice of parameters - The solidity
Even if the solidity is a key parameter for the performances of the machine, keeping into a reasonable range suggested by the theory, it not influences too much the efficiency.
From the analysis of the previous graphs seems reasonable to pick a value of the solidity of 1.225;
Solidity σ = 1.225
2.4 2.6 2.8 3
0.94
0.93
0.92
0.91
0.9
0.89
0.88
0.87
0.86
0.85
0.84
0.83
0.6 0.8 1 1.2 1.4 1.6 1.8 2 2.2
solidity
etaTT
nStages = 1
nStages = 2
nStages = 3
nStages = 4
nStages = 5
nStages = 6
nStages = 7
nStages = 8
38 of 62

## Slide 39: The choice of parameters - The solidity
Figure: Ainley criterion
Comparison of the solidity
with loading criterion of Ainley. As we see in figure 4 the value that we take is very similar
to that predicted by the Ainley loading criterion.

## Slide 40: The choice of parameters - The reaction degree
The reaction degree at midspan is also a relevant parameter.
If too low, the stator is too loaded.
If too high the load is mainly on the rotor.
From the theory we know that a mean between this two extreme condition let to have a good result.
So we check what is the reaction degree that gives the better performances around χ = 0.5.

## Slide 41: The choice of parameters - The reaction degree
A good value for χ seams to be 0.47, just a bit less than 0.5.
0.82
0.83
0.84
0.85
0.86
0.87
0.88
0.89
0.9
0.91
0.94
0.93
0.92
0.36 0.38 0.4 0.42 0.44 0.46 0.48 0.5 0.52 0.54
chiMID
etaTT
nStages = 1
nStages = 2
nStages = 3
nStages = 4
nStages = 5
nStages = 6
nStages = 7
nStages = 8
0.85
0.86
0.87
0.88
0.89
0.9
0.91
0.92
0.93
0.94
0.36 0.38 0.4 0.42 0.44 0.46 0.48 0.5 0.52 0.54
chiMID
etaTT
 |  |  |  |  |  |  |  | n = 3000 n = 4500 n = 6000 n = 7500 n = 9000 n = 10500 n = 12000 |  |  | 

## Slide 42: The choice of parameters - The reaction degree
It is also interesting to analyse the graphs in a reverse way, to start to check the best value for the number of stages and the rotational speed.
1
2 3
4
5
6
7
8
0.87
0.88
0.89
0.9
0.91
0.92
0.93
0.94
etaTT
chiMID = 0.5
 |  |  | chiMID |  |  | = | 0.35 | 
 |  |  | chiMID |  |  | = | 0.4 | 
 |  |  | chiMID |  |  | = | 0.45 | 
 |  |  | chiMID |  |  | = | 0.55 | 
0.3 0.45 0.6 0.75 0.9 1.05 1.2
0.85
0.87
0.86
0.9
0.89
0.88
0.91
0.93
0.92
0.94
etaTT
chiMID = 0.45
 |  |  | chiMID = 0.35 chiMID = 0.4 |  |  | 
 |  |  | chiMID = 0.5 chiMID = 0.55 |  |  | 
·104
nStages
rotational speed(rpm)
42 of 62

## Slide 43: The choice of parameters - Clearance and seals
From 1 to 2 seals we have a good increase in efficiency that is decreases so we take 2 seals per rotor.
2
4
6
8
10
0.96
0.95
0.94
0.93
0.92
0.91
0.9
0.89
0.88
0.87
0.86
0.85
0.84
0.83
0.82
etaTT
nStages = 1
nStages = 2
nStages = 3
nStages = 4
nStages = 5
nStages = 6
nStages = 7
nStages = 8
2
3
4
8
0.82
1
0.96
0.95
0.94
0.93
0.92
0.91
0.9
0.89
0.88
0.87
0.86
0.85
0.84
0.83
etaTT
sealsnum = 1
sealsnum = 2
sealsnum = 3
sealsnum = 4
sealsnum = 5
sealsnum = 6
sealsnum = 7
sealsnum = 8
sealsnum = 9
sealsnum = 10
5 6 7
nStages
sealsnum
43 of 62

## Slide 44: The choice of parameters - Clearance and seals
Decreasing the clearance the efficiency increases. We take as clearance k ≈ 0.02 · b ≈ 0.5 mm.
0.2
0.4
0.6
0.8
1
0.84
0.85
0.86
0.87
0.88
0.89
0.9
0.91
0.92
0.93
0.96
0.95
0.94
etaTT
n = 3000
n = 4500
n = 6000
n = 7500
n = 9000
n = 10500
n = 12000
0.2
0.4
0.6
0.8
1
0.95
0.94
0.93
0.92
0.91
0.9
0.89
0.88
0.87
0.86
0.85
0.84
0.83
0.82
0.81
0.8
etaTT
nStages = 1
nStages = 2
nStages = 3
nStages = 4
nStages = 5
nStages = 6
nStages = 7
nStages = 8
·10−3
·10−3
clearance
clearance
44 of 62

## Slide 45: The choice of parameters - Stages and speed
For any number of stages exists a proper value of the rotational speed that let to reach almost the same efficiency. Critical decision:
⇒ at 3000rpm, good efficiency for over 10 stages.
⇒ for 2 stages, good efficiency for n above 10000 rpm.
0.4
0.6
0.8
1
1.2
104
0.95
0.94
0.93
0.92
0.91
0.9
0.89
0.88
0.87
0.86
0.85
0.84
0.83
0.82
0.81
0.8
0.79
0.78
0.77
0.76
0.75
n
etaTT
nStages = 1
nStages = 2
nStages = 3
nStages = 4
nStages = 5
nStages = 6
nStages = 7
nStages = 8
2
4
6
10 12
14
0.95
0.94
0.93
0.92
0.91
0.9
0.89
0.88
0.87
0.86
0.85
0.84
0.83
0.82
0.81
0.8
0.79
0.78
0.77
0.76
0.75
8
nStages
etaTT
n = 3000
n = 4500
n = 6000
n = 7500
n = 9000
n = 10500
n = 12000
45 of 62

## Slide 46: The choice of parameters - Stages and speed and phi
For φ = 0.4469 we have the optimal efficiency at:
⇒ 4 stages;
⇒ n = 6000 rpm;
0.4469 0.6
0.8
1
1.2
1.4
0.85
0.86
0.87
0.88
0.89
0.9
0.91
0.92
0.93
0.94
phi
etaTT
 |  |  |  | nStages = 3 nStages = 4 nStages = 5 |  | 
0.4469 0.6
0.8
1
1.2
1.4
0.86
0.87
0.88
0.89
0.9
0.91
0.92
0.93
0.94
phi
etaTT
 |  |  |  |  | n = 4000 n = 4500 n = 5000 n = 5500 n = 6000 n = 6500 n = 7000 |  | 

## Slide 47: The design of the blades
0 0.2 0.4 0.6 0.8 1 1.2 1.4 1.6 1.8 2 2.2
−0.2
The blades are designed according two different rules:
NACA 4-digits for the mean line;
A3K7 for the thickness.
0.6
0.4
0.2
0
Figure: Example of a rotor blade with max thickness over chord of 0.2

## Slide 48: The design of the blades - The mean line
Calling m the maximum of the mean line and p the position between 0 and 1 at which the maximum is present, the equation of the mean line are represented by a parabola.
B =





m p2
2
(2 p x − x ) for x < p
m
(1 − p)
2
2
(1 − 2 p + 2 p x − x ) for x ≥ p
The advantage of this approach is that we can easily calculate everything we want of the mean line like the slope or the osculating circle radius.
It is reasonable to take p = 0.4.

## Slide 49: The design of the blades - The mean line
We miss the parameter m.
We can obtain it from the camber angle required and from p.
0 1
tan θ = tan(α + α ) =
tan α0 + tan α1
1 − tan α0 tan α1
(32)
Where tan α0 = 2 m and tan α1 = 2 m .
p 1−p
Finally m is the solution of the following equation.
4 tan(θ) m2 + 2 m + p (p − 1) · tan θ = 0
(33)

## Slide 50: The design of the blades - The thickness
Since the points are quite rough we apply a spline interpolation to get a smoother profile.
To find the top and bottom points of the blade we project the thickness perpendicular to the mean line
xup = x − t · sin(tan−1(yc' ))
yup = x + t · sin(tan−1(yc' ))
xdown = x + t · sin(tan−1(yc' )) (34)
ydown = x − t · cos(tan−1(yc' )) (35)
x/c(%) | 0 | 1.25 | 2.5 | 5 | 10 | 15 | 20 | 25 | 30 | 35 | 40 45
t/c | 0 | 3.469 | 4.972 | 6.916 | 9.007 | 9.827 | 10 | 9.699 | 9.613 | 9.106 | 8.594 7.913
x/c(%) | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100
t/c | 7.152 | 6.339 | 5.5 | 4.661 | 3.846 | 3.067 | 2.406 | 1.83 | 1.367 | 1.101 | 0
Table: Thickness along the mean line.

## Slide 51: The design of the blades - The deviation
Even if the blades drive the flow, at the trailing edge we have just one side that keep it in the desired direction.
⇒ The flow deviates.
Theroretical 1D approach can provide the result, but the semi-experimental correlations are more reliable.
Ainley and Mathieson provide a correlation for the deviation given:
the geometrical angle;
the curvature of the suction side e2;
the mach number if greater than 0.5.
2We approximate it by computing the radius of the circumference passing
through the last 3 points of the mean line.

## Slide 52: The design of the blades - The deviation
We know how to calculate the real flow angle from the geometrical angle but we are interested in the opposite process.
We need a specific flow angle that provides the work required by the compression.
⇒ We want to know the geometric angle of the blade.
s
geom
)
αflow = f (αgeom) − 4 e(α (36)
In the case M is greater than 0.5 we must apply a further correction. We solve equation 36 by applying the secants method.
From that solution ⇒ design the blade that provides the required work also accounting for the deviation angle.

## Slide 53: The results - Losses
Losses of the four stages for the stators and the rotors.
1
2
3
4
0
2
4
6
8
10
Stage
Losses in %
Profile losses Secondary losses Clearance losses
1
2
3
4
0
2
4
6
8
10
Stage
Losses in %
Profile losses Secondary losses Clearance losses

## Slide 54: The results - Profile losses along the span
Losses of the four stages for the stators and the rotors.
0
0.2
0.8
1
1.6
1.7
1.8
1.9
2
2.1
0.4 0.6
Span coordinate
Profile losses (in %)
Stator 1
Stator 2
Stator 3
Stator 4
0
0.2
0.8
1
1.5
1.52
1.54
1.56
1.58
1.6
0.4 0.6
Span coordinate
Profile losses (in %)
Rotor 1
Rotor 2
Rotor 3
Rotor 4
54 of 62

## Slide 55: The results - TS transformation
Representation of the stages in the T-S plane and the comparison with the liquid vapour curve.
2
4
6
8
10
0
0
200
400
600
800
1,000
Entropy s
Temperature T (K)
6.96 6.97
800
820
840
860
880
900
920
960
940
6.97 6.98 6.98 6.99
Entropy s
Temperature T (K)
54 of 62

## Slide 56: The results - The temperature
0.54
0.53
0.52
0.51
0.5
0.49
960
940
920
900
880
860
840
0.48
0
1
2
3
4
5
6
10−2
56 of 62

## Slide 57: The results - The pressure
0.54
0.53
0.52
0.51
0.5
0.49
140
130
120
110
100
90
80
70
0.48
0
1
2
3
4
5
6
10−2
56 of 62

## Slide 58: The results - The density
0
1
2
3
4
5
6
10−2
0.48
0.49
0.5
0.51
0.52
0.53
0.54
18
20
22
24
26
28
30
32
34
58 of 62

## Slide 59: The results - The cascade
0
2
4
6
8
10
12
14
0
2
4
6
8
10
62 of 62

## Slide 60: Table: Stator properties
Stage | Blades | Solidity | β | Blade h.(m) | Inlet M | Cp
1 | 156 | 1.219 | 1.121 | 0.025 | 0.194 | 2524.1
2 | 131 | 1.217 | 1.124 | 0.027 | 0.463 | 2480.5
3 | 110 | 1.223 | 1.130 | 0.033 | 0.473 | 2437.8
4 | 91 | 1.220 | 1.136 | 0.039 | 0.484 | 2395.9
Table: Rotor properties
Stage | Blades | Solidity | β | Blade h.(m) | Inlet Mw | Cp
1 | 143 | 1.223 | 1.110 | 0.025 | 0.198 | 2501.2
2 | 119 | 1.214 | 1.114 | 0.030 | 0.202 | 2458.2
3 | 99 | 1.214 | 1.119 | 0.036 | 0.207 | 2415.8
4 | 82 | 1.218 | 1.125 | 0.043 | 0.212 | 2374.3
Table: Stage properties
Stage | χ | ηT T | β | βT T
1 | 0.461 | 0.927 | 1.244 | 1.240
2 | 0.465 | 0.930 | 1.252 | 1.251
3 | 0.465 | 0.933 | 1.264 | 1.263
4 | 0.465 | 0.936 | 1.278 | 1.276
Total | - | 0.936 | 2.518 | 2.500
62 of 62

## Slide 61: Further develops
Compare constant angle with other methodologies;
Iterate to guarantee the required work along the span;
Different solidity for the rotor and the stator;
Variable χ with stages (lower in the first stages);
Off-design performances;
Mechanical analysis
  Optimize rotor internal diameter.
  Vibration analysis and natural frequencies.
Apply more refined losses correlation.
Clearance design;
Cost/performance comparison between 3000 and 6000 rpm.
62 of 62

## Slide 62
62 of 62